Rockville Pipeline Company

Customer Awareness- Cross Connections and Backflow Prevention

In our industrial world, many things present a potential source of pollution to our drinking water.  Pesticides and herbicides that are used in agricultural and residential activities, mining, manufacturing, automobiles, and the list goes on.  Because of this potential contamination to our drinking water, all water systems are required to take samples to be analyzed by a certified laboratory to determine if the water is safe for consumption.

But after all this is done, another hazard to our water exists in the form of Cross-Connections.  These are simply physical connections that create a route between our drinking water systems and contaminates that might enter into the system.  A common occurrence of a cross connection is a garden hose.  If this hose is placed into a water trough for example, it then creates the potential for the water in the trough to be siphoned back into the system, should the pressure in the system drop below atmospheric pressure due to maintenance or failure of the water system because of a break in the main line, etc.  This is referred to as “back-siphonage”.  There are also other ways that undesirable or hazardous contaminates can enter into the system;  Mechanical pumps that  are connected to the system, and operate at a higher pressure than the system pressure, such as you find at car washes, can malfunction and pump back into the system.  This is referred to as “backpressure”.   Many devices exist today that can help protect these type of connections from polluting our drinking water.  They form a physical barrier that, when properly installed and maintained, stop undesirable contaminates from entering into the water system.  However, the most effective tool is an informed and conscientious customer who knows what to look for and how to eliminate these types of connections whenever possible.

The following pages provide some information and illustrations that will help you understand the different types of cross-connections, types of protection, and how we can prevent or protect against them.

If you have any questions concerning cross-connections within your system, please contact Rockville Pipeline Company by email: pipeline@infowest.com.

Appendix A

# Partial List of Plumbing Hazards

| Fixtures with Direct Connections Description Air conditioning, air washer Air conditioning, chilled water Air conditioning, condenser water Air line Aspirator, laboratory Aspirator, medical Aspirator, weedicide and fertilizer sprayer Autoclave and sterilizer Auxiliary system, industrial Auxiliary system, surface water Auxiliary system, unapproved well supply Boiler system Chemical feeder, pot-type Chlorinator Coffee urn Cooling system Dishwasher Fire standpipe or sprinkler system Fountain, ornamental Hydraulic equipment Laboratory equipment Lubrication, pump bearings Photostat equipment Plumber’s friend, pneumatic Pump, pneumatic ejector Pump, prime line Pump, water operated ejector | Sewer, sanitary Sewer, storm Swimming pool Fixtures with Submerged Inlets Description Baptismal fount Bathtub Bedpan washer, flushing rim Bidet Brine tank Cooling tower Cuspidor Drinking fountain Floor drain, flushing rim Garbage can washer Ice maker Laboratory sink, serrated nozzle Laundry machine Lavatory Lawn sprinkler system Photo laboratory sink Sewer flushing manhole Slop sink, flushing rim Slop sink, threaded supply Steam table Urinal, siphon jet blowout Vegetable peeler Water closet, flush tank, ball cock Water closet, flush valve, siphon jet |
| --- | --- |

38  •

Appendix B

| Illustrations of Backsiphonage The following illustrates typical plumbing installations where backsiphonage is possible. Backsiphonage Case I (Fig. 44) - Contact Point: A rubber hose is submerged in a bedpan wash sink. - Causes of Reversed Flow:(I) A sterilizer connected to the water supply is allowed to cool without opening the air vent. As it cools, the pressure within the sealed sterilizer drops below atmospheric producing a vacuum which draws the polluted water into the sterilizer contaminating its contents. (2) The flushing of several flush valve toilets on a lower floor which are connected to an | undersized water service line reduces the pressure at the water closets to atmospheric producing a reversal of the flow. C. Suggested Correction: The water connection at the bedpan wash sink and the sterilizer should be provided with properly installed backflow preventers. Backsiphonage Case 2 (Fig. 45) - Contact Point: A rubber hose is submerged in a laboratory sink. - Cause of Reversed Flow:Two opposite multi-story buildings are connected to the same water main, which often lacks adequate pressure. The building on the right has installed a booster pump. |
| --- | --- |

A

B

B

B

A

B

Backsiphonage (Case 1).

FIGURE 45.

Backsiphonage (Case 2).

FIGURE 44.

When the pressure is inadequate in the main, the building booster pump starts pumping, producing a negative pressure in the main and causing a reversal of flow in the opposite building.

C. Suggested Correction: The laboratory sink water outlet should be provided with a vacuum breaker. The water service line to the booster pump should be equipped with a device to cut off the pump when pressure approaches a negative head or vacuum.

## Backsiphonage

Case 3 (Fig. 46)

- Contact Point: A chemical tank has a submerged inlet.

- Cause of Reversed Flow:The plant fire pump draws suction directly from the city water supply line which is insufficient to serve normal plant requirements and a major fire at the same time. During a fire emergency, reversed flow may occur within the plant. C. Suggested Correction: The

## Backsiphonage

Case 4 (Fig. 47)

- Contact Point: The water supply to the dishwasher is not protected by a vacuum breaker. Also, the dishwasher has a solid waste connection to the sewer.

- Cause of Reversed Flow:The undersized main serving the building is subject to reduced pressures, and therefore only the first two floors of the building are supplied directly with city pressure. The upper floors are served from a booster pump drawing suction directly from the water service line. During periods of low city pressure, the booster pump suction creates negative pressures in the low system, thereby reversing the flow.

- Suggested Correction: The dishwasher hot and cold water should be supplied through an air gap and the waste from the dishwasher should discharge through an indirect waste. The booster pump should be equipped with a low-pressure cutoff device.

## Backsiphonage

Case 5 (Fig. 48)

- Contact Point: The gasoline storage tank is maintained full and under pressure by means of a direct connection to the city water distribution system.

FIGURE 48.

Backsiphonage (Case 5).

B

A

Main

Gasoline

Water

FIGURE 49.

Backsiphonage (Case 6).

- Cause of Reversed Flow:Gasoline may enter the distribution system by gravity or by siphonage in the event of a leak or break in the water main.

- Suggested Correction: A reduced pressure principle backflow preventer should be installed in the line to the gasoline storage tank or a surge tank and pump should be provided in that line.

## Backsiphonage

Case 6 (Fig. 49)

- Contact Point: There is a submerged inlet in the second floor bathtub.

- Cause of Reversed Flow:An automobile breaks a nearby fire hydrant causing a rush of water and a negative pressure in the service line to the house, sucking dirty water out of the bathtub.

- Suggested Correction: The hot and cold water inlets to the bathtub should be above the rim of the tub.

water service to the chemical tank should be provided through an air gap.

APPENDIX B  •  39

Backflow

Case 2 (Fig. 51)

Backflow

B

A

FIGURE 51.

Backflow (Case 2).

Appendix C

# Illustrations of Backpressure

The following presents illustrations of typical plumbing installations where backflow resulting from backpressure is possible.

## Backflow

Case I (Fig. 50)

A. Contact Point: A direct connection from the city supply

to the boiler exists as a safety

measure and for filling the	A. Contact Point: Sewage system. The boiler water system	seeping from a residential is chemically treated for scale	cesspool pollutes the private

| prevention and corrosion control. - Cause of Reversed Flow:The boiler water recirculation pump discharge pressure or backpressure from the boiler exceeds the city water pressure and the chemically treated water is pumped into the domestic system through an open or leaky valve. - Suggested Correction: As minimum protection two check valves in series should be provided in the makeup waterline to the boiler system. An air gap separation or reduced pressure principle backflow preventer is better. | well which is used for lawn sprinkling. The domestic water system, which is served from a city main, is connected to the well supply by means of a valve. The purpose of the connection may be to prime the well supply for emergency domestic use. - Cause of Reversed Flow:During periods of low city water pressure, possibly when lawn sprinkling is at its peak, the well pump discharge pressure exceeds that of the city main and well water is pumped into the city supply through an open or leaky valve. - Suggested Correction: The |
| --- | --- |

C. Suggested Correction: Each pier water outlet should be protected against backflow. The main water service to the pier should also be protected against backflow by an air gap or reduced pressure principle backflow preventer.

Backflow

Case 4 (Fig. 53)

- Contact Point: A singlevalved connection exists between the public, potable water supply and the firesprinkler system of a mill.

- Cause of Reversed Flow:The sprinkler system is normally supplied from a nearby lake through a high-pressure pump. About the lake are large

| Case 3 (Fig. 52) - Contact Point: A valve connection exists between the potable and the non potable systems aboard the ship. - Cause of Reversed Flow:While the ship is connected to the city water supply system for the purpose of taking on water for the potable system, the valve between the potable and nonpotable systems is | numbers of overflowing septic tanks. When the valve is left open, contaminated lake water can be pumped to the public supply. C. Suggested Correction: The potable water supply to the fire system should be through an air gap or a reduced pressure principle backflow preventer should be used. |
| --- | --- |
| opened, permitting contaminated water to be pumped into the municipal supply. | FIGURE 53. Backflow (Case 4). |

ACME MILLS

Sprinkler

System

B

A

FIGURE 52.

Backflow (Case 3). connection between the well water and city water should be broken

A

B

City

main

Pump

To potable

system

FIGURE 50.

Backflow (Case 1).

Chemical feeder

B

A

40

•

Appendix D

# Illustrations of Air Gaps

The following illustrations describe methods of providing an air gap discharge to a waste line which may be occasionally or continuously subject to backpressure.

2

xD

Pump

Ball check

Waste line

D

FIGURE 54.

Air gap to sewer subject to

backpressure—force main.

FIGURE 55. Air gap to sewer subject to backpressure—gravity drain.

2

xD

Indirect waste

Ball check

Support vanes

Horizontal waste

D

FIGURE 56.

Fire system makeup tank for a dual water system.

To fire system

Float valves

Nonpotable supply

2

xD

Potable supply

Appendix E

# Illustrations of Vacuum Breakers

FIGURE 57.

Vacuum breakers.

Brass inset

Rubber sleeve

Air vent

contaminated liquids

Vaccum closes gate

Cowl nut

Flush connection

Air enters here	Air

preventing rise of in fixtures

FIGURE 58.

Vacuum breaker arrangement for an outside hose hydrant.

Plan

“A”

“A”

Exterior

building wall

1

"

sleeve, sch. 40.

Hand wheel

I.P.S. hose adapte

r

Coupling M.I. galv.

Section “A” “A”

½

"

or ¾

"

Ell. m. M. I. galv.

½

"

or ¾

"

nipple galv.

½

"

or ¾

"

gate valve

½

"

or ¾

"

sch. 40. galv.

½

"

or ¾

"

vacuum breaker

(By permission of Mr. Gustave J. Angele

Sr., P.E. formerly Plant Sanitary

Engineer, Union Carbide Nuclear

Division, Oak Ridge, Tenn.)

APPENDIX E  •  41